## Slide 1: Electrical Machinery Fundamentals
1
EE 250 SPRING 2020
Lecture 7

## Slide 2: Chapter 11 Special Transformers

## Slide 3
Transformer Basics

## Slide 4: 11.1 Dual-voltage distribution transformer
Residential transformers generally have two secondary windings (in series) with total line voltage of 240 V
Central tap called neutral is connected to ground along with H2 (primary winding)
Characteristics:
  Nominal rating ranges from 3kVA to 500kVA
  Mounted on poles
  Supply power to approx. 20 customers
  Load on distribution transformer varies depending upon demand
  When load peaks occurs? Power peaks less than 1 or 2 hours and for rest of day transformer operate far below their normal rating
  Efforts are made to keep the no-load losses small => Low-loss silicon-steel in the core

## Slide 5: 11.1 Dual-voltage distribution transformer

## Slide 6: 11.2 Autotransformer
In such a transformer secondary winding is a part of primary winding and there is no need of separate secondary winding
Benefits: Smaller, lighter and cheaper than standard transformer of equal output power
Drawback: Absence of electrical isolation between primary and secondary
Single transformer winding having N1 turns on an iron core
Winding connected to fixed AC voltage source E1 and exciting current Io creates an AC flux Φm in iron core
Tap C is taken off the winding => N2 turns between C and A
As induced voltage is proportional to the no. of turns, so:

## Slide 7: 11.2 Autotransformer
Primary voltage E1, Secondary voltage E2
Primary terminals B,A and Secondary terminals C,A are no longer isolated from each other because of common terminal A
Resultant current I2 upon load connection across secondary terminal causes primary current I1 to flow
BC portion carries current I1 and according to KCL CA portion carries (I2 – I1) and also mmf due to I1 and (I2 – I1) must be equal and opposite and thus we have:
  To transform when primary/secondary ratio is close to 1
=>

## Slide 8: 11.2 Autotransformer
Assuming transformer losses and exciting current are negligible => Apparent power drawn by load=Apparent power supplied by source. So:
Applications:
  Used to start induction motors
  To regulate voltage of transmission lines
  To transform when primary/secondary ratio is close to 1
=>
Example 11.1

## Slide 9: 11.2 Autotransformer

## Slide 10: 11.3 Conventional transformer connected as an autotransformer
Conversion to autotransformer by connecting primary and secondary windings of conventional transformer in series.
Depending upon connections, secondary voltage can be added to or subtracted from the primary voltage.
Basic operation remains unchanged by changing connection

## Slide 11: 11.4 Voltage transformers
High-precision transformers in which ratio of primary voltage to secondary voltage is a known constant
Secondary voltage almost in phase with primary and nominal secondary voltage is usually 115V that permits standard instruments to be used on secondary side
Used to measure or monitor the voltage on transmission line and to isolate the metering equipment from these lines

## Slide 12: 11.4 Voltage transformers
Construction: Same as that of conventional transformer but insulation between primary and secondary must be great to withstand full line voltage on HV side
Distributed capacitance makes invisible connection between primary and secondary windings and thus produce very high voltage between S.W and ground
One terminal of S.W is connected to ground for safety from fatal shock and to limit the highest voltage between S.W and ground to a value of 115V
Voltage transformers are installed on HV lines to measure line-to-neutral voltage

## Slide 13: 11.5 Current transformer
High-precision transformers in which ratio of primary to secondary current is a known constant with small change upon loading
Phase angle between primary and secondary current is usually much less than one degree
Used to measure/monitor the line current and to isolate the metering equipment from these lines
Nominal secondary current is usually 5A, irrespective of the primary current rating
Like conventional transformer, current ratio is inversely proportional to number of turn on P.W & S.W

## Slide 14: 11.5 Current transformer
For safety CT must always be used for measuring currents in HV transmission lines
Insulation between P.W & S.W must be great enough to withstand full line-to-neutral voltage
Maximum voltage that CT can withstand is mentioned on the nameplate
Like voltage transformer one S.W is always connected to ground
Example: Handheld current transformers

## Slide 15: 11.5 Current transformer

## Slide 16: 11.6 Opening the secondary of CT can be dangerous
Never open the secondary circuit of CT while current is flowing through primary circuit
Secondary of CT opened => Primary current flows unchanged because impedance of primary is negligible compared to that of electrical load
Due to open secondary there is no more bucking effect and thus line current becomes exciting current of transformer
Flux is so large that core is totally saturated for the greater part of every half cycle
From fig. as current rises or falls in first half cycle, flux Φ in the core also rises and falls but it remains at fix saturation level Φs for most of the time and same is the case for second half cycle
Dangerous situation for being getting shock

## Slide 17: 11.6 Opening the secondary of CT can be dangerous

## Slide 18: 11.7 Toroidal current transformers
Consist of laminated ring-shaped core that carries secondary winding
Primary is composed of single conductor passing through center of S.W core
If secondary possesses N turns then ratio of transformation is N because primary consist of 1 turn
When line current exceeds 100A, we use totoidal transformer
Inexpensive and widely used in low-voltage and medium-voltage indoor installations
Applications:
  Circuit-breaker

## Slide 19: 11.8 Variable autotransformer
Used when we wish to obtain variable AC voltage from a fixed source
Composed of single-layer winding wound uniformly on a toroidal iron core
Movable carbon brush serves as a variable tap
Brush position ranges from 0° to 330°
Secondary voltage depends upon the position of carbon brush
E1 fixed connection to 90% tap => E2 varies from 0 to 110%
Efficient and provide good voltage regulation under variable load
Secondary is protected by fuse so that I2 must not exceed the current rating of the transformer

## Slide 20: 11.9 High-impedance transformers
Reactance is a form of opposition that electronic components exhibit to the passage of alternating current because of capacitance or inductance
Transformers that have been studied in previous slides have low leakage reactance (.03 to 0.1 per unit)
Industrial & commercial applications requires much higher reactance (up to 0.9 per unit)
  Application of High-Impedance transformers:
Electric Toys:
  Toy accidentally short-circuited
  Neither practical nor safe to protect with fuse
  Transformer design with high leakage reactance such that permanent short-circuit across low-voltage secondary will not cause overheating
  Bell transformers that provide low-voltage signaling power to home, current is limited by high reactance in case of short-circuiting on secondary side

## Slide 21: 11.9 High-impedance transformers
Arc welders:
  Negative E/I characteristics (=> When arc is struck, current increases as voltage falls) for electric arc furnaces & discharges in gases
  Addition of impedance in series with load to maintain steady arc or uniform discharge
  Series impedance:
    Resistor
    Reactor (Preferable as consumes little active power)
  Economical to incorporate the reactance (high leakage reactance) in the transformer in case we wish to use transformer to supply the load
  Example:
  Neon sign transformer
    P.W P
    Two S.Ws in series with neon tube
    Flux increase => Current increases => Voltage falls

## Slide 22: 11.9 High-impedance transformers
Electric Arc Furnaces:
  Generates heat by maintaining intense arc between two carbon electrodes
  Relatively low secondary voltage is used
  Large secondary current is limited by leakage reactance of the transformer
  Leakage reactance of secondary along with reactance of conductor must be sufficient to provide limiting impedance in large furnaces
Arc-welding transformers:
  Have high leakage reactance to stabilize the arc during the welding process
  Open circuit voltage (about 70 V) for striking arc
  With established arc secondary voltage falls to about 15 V

## Slide 23: 11.9 High-impedance transformers
Three-phase static var compensator:
  Intentionally designed to produce leakage flux
  Primary & Secondary are loosely coupled
  P.W (230 to 765 kV) & S.W (typically 6kV)
  S.W is connected to controller to control secondary current flow that results in varying the leakage flux accordingly

## Slide 24: 11.10 Induction heating transformers
High frequency (500 Hz) AC source connected to P.W that surrounds large crucible containing molten metal (S.W short-circuited upon itself and carries large secondary current)
Large current provides energy and keeps the metal in molten state
If source with high value is to be used then we lowers the frequency of source accordingly
Power factor of coreless induction furnaces is very low (about 20 %)
  Reason:
    Large magnetizing current requirement for driving flux through molten metal and air

## Slide 25: 11.10 Induction heating transformers
Channel furnaces:
  Having laminated iron core linked with channel of molten metal
  Ceramic channel fitted at bottom of crucible
  P.W is excited by 60 Hz source
  Secondary current flows through molten metal
  Channel is behaving as single turned secondary winding
  Magnetizing current is low as flux is confined to highly permeable iron core
  Leakage flux is large as P.W and S.W are not tightly coupled
  Higher power factor (60 to 80%)

## Slide 26: 11.11 High-frequency transformers
Higher frequency helps us in reducing size of devices such as transformers, inductors and capacitors
  Example: Practical transformer to understand the size variation with increasing frequency
Stepwise Sequence:
  Raise frequency
  Lower flux density due to increased losses
  Raise flux density by introducing special core material
  In order to maintain original voltage ratio of 120V to 24V we need to rewind the transformer and new primary and secondary turn will be 45 and 9 respectively, this can be calculated as:
  Reduction in number of turns will result in increase of wire size
  Capacity of transformer is still 480VA => Primary and secondary current must be raised to 4A and 20A respectively
Advantages:
  Smaller, Cheaper, Efficient, Lighter than 60Hz transformer

## Slide 27
Peak flux will change as under by increasing
flux density from 0.04T to 0.2T:
Special Nickle Steel Insulation

## Slide 28: Chapter 11 11.1-11.11 Examples: 11.1 & 11.3